WPH600 Series

pH/ORP/ISE Controllers

Part 1.		General

1.1	Scope

A.	This section describes the requirements for a multiple input/output pH/ORP/ISE controller.

B.	Under this item, the contractor shall furnish and install the

pH/ORP/ISE control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the 				submittal for this section:

1.	Data sheets and catalog literature for the pH/ORP/ISE controller and sensors.

2.	Interconnection and dimensional drawings.

3.	List of spare parts

Part 2.		Products

2.1	pH/ORP/ISE controller

A.	The pH/ORP/ISE control system shall be a capable of measuring system pH/ORP/ISE and temperature. An optional second sensor shall be a choice of conductivity, pH, ORP, ISE, PTSA, free chlorine, total chlorine, chlorine dioxide, ozone, Peracetic acid, or hydrogen peroxide. The conductivity sensors shall be either a contacting style or an electrodeless style. Six digital inputs are available for sensors that shall include a flow switch, contacting water meter, paddlewheel flowmeter or other dry contact devices. Outputs shall include six relays, and two optional 4-20 mA outputs. Optional digital communications shall be via Ethernet. The controller shall be accessible via the Internet for configuring, data logging, and control of relay outputs. The USB port shall provide the ability to upgrade the software in the controller to the latest version, save all the set points from a controller onto a USB flash disk and import settings into another W600 controller, and download datalog files to a USB flash disk. On screen graphing of one analog signal and one digital signal/relay state shall be available on the touchscreen display.

B.	Control Module:

- Enclosure: Polycarbonate Resin, NEMA 4X, lockable hinged door.

2.	Power:		100-240 VAC  10%, 50 or 60 Hz

3.	Inputs:

| Sensor Input Signals (0, 1 or 2 depending on model code) |  |
| --- | --- |
| Contacting Conductivity | 0.01, 0.1, 1.0, or 10.0 cell constant OR |
| Electrodeless Conductivity | OR |
| Disinfection | OR |
| Amplified pH/ORP/ISE | Requires a preamplified signal. Walchem WEL or WDS series recommended. ±5VDC power available for external preamps. |
| Each sensor input card contains a temperature input |  |
| Temperature | 100 or 1000 ohm RTD, 10K or 100K Thermistor |
| Analog (4-20 mA) Sensor Input (0, 2 or 4 depending on model code) |  |
|  | 2-wire loop powered or self-powered transmitters supported 3 or 4 –wire transmitters supported Each sensor input board has two channels Channel 1, 130 ohm input resistance Channel 2, 280 ohm input resistance |
| Available Power | Two independent isolated 24 VDC ± 15% supplies per board 1.5 W maximum for each channel 2W (83 mA at 24 VDC) total power consumption for all channels (four total channels if two boards are installed; 2W is equivalent to 2 Little Dipper sensors) |
| Digital Input Signals (6): |  |
| State-Type Digital Inputs | Electrical: Optically isolated and providing an electrically isolated 9V power with a nominal 2.3mA current when the digital input switch is closed Typical response time: < 2 seconds Devices supported: Any isolated dry contact (i.e. relay, reed switch) Types: Interlock |
| Low Speed Counter-Type Digital Inputs | Electrical: Optically isolated and providing an electrically isolated 9V power with a nominal 2.3mA current when the digital input switch is closed 0-10 Hz, 50 msec minimum width Devices supported: Any device with isolated open drain, open collector, transistor or reed switch Types: Contacting Flowmeter |
| High Speed Counter-Type Digital Inputs | Electrical: Optically isolated and providing an electrically isolated 9V power with a nominal 2.3mA current when the digital input switch is closed, 0-250 Hz, 1.25 msec minimum width Devices supported: Any device with isolated open drain, open collector, transistor or reed switch Types: Paddlewheel Flowmeter |

- Outputs:

| Powered mechanical relays (0 or 6 depending on model code): |  |
| --- | --- |
|  | Pre-powered on circuit board switching line voltage |
|  | 6 A (resistive), 1/8 HP (93 W) |
|  | All six relays are fused together as one group, total current for this group must not exceed 6A |
| Dry contact mechanical relays (0, 2 or4 depending on model code): |  |
|  | 6 A (resistive), 1/8 HP (93 W) |
|  | Dry contact relays are not fuse protected |

| Pulse Outputs (0, 2 or4 depending on model code): |  |
| --- | --- |
|  | Opto-isolated, Solid State Relay |
|  | 200mA, 40 VDC Max. |
|  | VLOWMAX = 0.05V @ 18 mA |
| 4 - 20 mA (0 or 2) | Internally powered |
|  | Fully isolated |
|  | 600 Ohm max resistive load |
|  | Resolution 0.0015% of span |
|  | Accuracy ± 0.5% of reading |
| Ethernet | 10/100 802.3-2005 |
|  | Auto MDIX support |
|  | Auto Negotiation |

5.	Software features:

Six relay outputs may be set to a variety of control modes:

On/Off set point control

Time Proportional control

Pulse Proportional Control (requires pulse output relay option)

PID (requires pulse output relay option)

Dual set point

Probe wash

Timed activation triggered by a Water Contactor or Paddlewheel flow meter’s accumulated total flow

Activate with another output

Activate as a percent of another output’s on-time

Activation based upon the state of a contact closure

Activate as a percent of elapsed time

Daily, Weekly, 2-week or 4-week timers

Always on unless interlocked

Diagnostic Alarm

Manual activation of the relays shall be easily accomplished via the touchscreen, or a PC.

A maximum output on-time shall be available on the control relays to prevent runaway control.

Any relay may be reconfigured to any one of a number of control algorithms, responding to the signal from any input desired.

The optional analog inputs shall be configurable for level sensors, flowmeters, or any other type of 4-20 mA transmitter, providing appropriate units of measure and scaling.

The digital inputs shall be configurable for level switches, flowmeters, flow switches, or generic counting or interlocking operation.

The optional analog outputs shall be configurable for retransmitting a sensor signal or for proportional or PID control.

The controller set points may be entered by downloading them from one controller, and uploading them into another controller.

Access to the controller shall be possible using Ethernet, locally or via the Internet, or via the local touchscreen display, simultaneously if desired.

No proprietary software shall be required on the user’s computer to communicate with the controller, or to view or change set points.

C.	Sensors:

Contacting Conductivity

1.	Operating principle: The conductivity sensor shall be driven with a low voltage AC signal, and the return signal voltage will vary with the conductivity of the intervening solution. The temperature sensor within this sensor compensates for the effect of temperature on the conductivity signal.

2.	Materials of construction: Glass-Filled Polypropylene, Graphite or 316SS, FKM

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-150 psi

- Other materials and higher pressure sensors shall be made available.

Electrodeless Conductivity

1.	Operating principle: The conductivity sensor shall be driven with a low voltage AC signal, which induces a current in the surrounding liquid which varies in intensity with the conductivity of the liquid, which is picked up by the sensor and transmitted to the controller. The temperature sensor within this sensor compensates for the effect of temperature on the conductivity signal.

2.	Materials of construction: CPVC, FKM

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-150 psi

pH

1.	Operating principle: The pH sensor shall consist of a replaceable cartridge containing a pH sensitive glass and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module. The temperature signal from the conductivity sensor shall be used to compensate the pH reading as well.

2.	Materials of construction: Glass-Filled Polypropylene, CPVC, HDPE, FKM, Glass

3.	Process connections: ¾” NPTF

4.	Temperature range: 50-158 F, 10-70 C

- Pressure range: 0-100 psi

- Other materials and higher pressure sensors shall be made available.

ORP

1.	Operating principle: The ORP sensor shall consist of a replaceable cartridge containing a platinum electrode and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

2.	Materials of construction: Glass-Filled Polypropylene, CPVC, HDPE, FKM, Glass, and Platinum.

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-100 psi

- Other materials and higher pressure sensors shall be made available.

DISINFECTION

- Operating principle: The oxidizer molecules diffuse through the membrane and in the acidic environment of the electrolyte fill solution, a redox reaction occurs at the electrodes in the sensor. The current generated by this reaction is converted to a robust voltage signal that is linear with the concentration of the oxidizer.

2.	Materials of construction: Glass-Filled Polypropylene, PVC, Silicone rubber, polycarbonate, 316SS, PEEK.

3.	Process connections: ¾” NPTF

4.	Temperature range: 41-113 F, 5-45 C (typical)

5. 	Pressure range: 0-14.7 psi (0-1 atmosphere)

D.	Controller and Sensor Performance

| 0.01 Cell Contacting Conductivity |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Range | 0-300 µS/cm |  |  |  |  |
| Resolution | 0.01 µS/cm, 0.0001 mS/cm, 0.001 mS/m, 0.0001 S/m, 0.01 ppm |  |  |  |  |
| Accuracy | ± 1% of reading |  |  |  |  |
| 0.1 Cell Contacting Conductivity |  |  |  |  |  |
| Range | 0-3,000 µS/cm |  |  |  |  |
| Resolution | 0.1 µS/cm, 0.0001 mS/cm, 0.01 mS/m, 0.0001 S/m, 0.1 ppm |  |  |  |  |
| Accuracy | ± 1% of reading |  |  |  |  |
| 1.0 Cell Contacting Conductivity |  |  |  |  |  |
| Range | 0-30,000 µS/cm |  |  |  |  |
| Resolution | 1 µS/cm, 0.001 mS/cm, 0.1 mS/m, 0.0001 S/m, 1 ppm |  |  |  |  |
| Accuracy | ± 1% of reading |  |  |  |  |
| 10.0 Cell Contacting Conductivity |  |  |  |  |  |
| Range | 0-300,000 µS/cm |  |  |  |  |
| Resolution | 10 µS/cm, 0.01 mS/cm, 1 mS/m, 0.001 S/m, 10 ppm |  |  |  |  |
| Accuracy | ± 1% of reading |  |  |  |  |
| pH |  |  | ORP |  |  |
| Range -2 to 16 pH units Resolution 0.01 pH units Accuracy ± 0.01% of reading |  |  | Range -1500 to 1500 mV Resolution 0.1 mV Accuracy ± 1 mV |  |  |
| Disinfection Sensors |  |  |  |  |  |
| Range (mV) -2000 to 1500 mV |  |  |  | Range (ppm) 0-2 ppm to 0-20,000 ppm |  |
| Resolution (mV) 0.1 mV |  |  |  | Resolution (ppm) Varies with range and slope |  |
| Accuracy (mV) ± 1 mV |  |  |  | Accuracy (ppm) Varies with range and slope |  |
| Temperature |  |  |  | Analog (4-20 mA) |  |
| Range 23 to 500°F (-5 to 260°C) |  |  |  | Range 0 to 22 mA |  |
| Resolution 0.1°F (0.1°C) |  |  |  | Resolution 0.01 mA |  |
| Accuracy ± 1% of reading |  |  |  | Accuracy ± 0.5% of reading |  |
| Electrodeless Conductivity |  |  |  |  |  |
| Ranges |  | Resolution |  |  | Accuracy |
| 500-12,000 µS/cm |  | 1 µS/cm, 0.01 mS/cm, 0.1 mS/m, 0.001 S/m, 1 ppm |  |  | ± 1% of reading |
| 3,000-40,000 µS/cm |  | 1 µS/cm, 0.01 mS/cm, 0.1 mS/m, 0.001 S/m, 1 ppm |  |  | ± 1% of reading |
| 10,000-150,000 µS/cm |  | 10 µS/cm, 0.1 mS/cm, 1 mS/m, 0.01 S/m, 10 ppm |  |  | ± 1% of reading |
| 50,000-500,000 µS/cm |  | 10 µS/cm, 0.1 mS/cm, 1 mS/m, 0.01 S/m, 10 ppm |  |  | ± 1% of reading |
| 200,000-2,000,000 µS/cm |  | 100 µS/cm, 0.1 mS/cm, 1 mS/m, 0.1 S/m, 100 ppm |  |  | ± 1% of reading |

E.	Indication

1.	Graphic User Interface

A 320 x 240 pixel monochrome backlit display with touchscreen shall indicate the process values, the status of outputs and alarms, and provide for all settings and calibrations.

Six LED lamps shall indicate the on/off status of the control outputs.

F.	Equipment

The pH/ORP/ISE controller shall be a Walchem WPH600 series.

Part 3.		Operator Functions

3.1	Calibration

- The sensor calibration shall be a one point process calibration, a two point buffer calibration, or a one point buffer calibration.

- All set points shall be set through the touchscreen, or via a PC connected either locally or remotely via Ethernet.

- Two levels of access codes shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- Each control output shall be able to be set to any of the available control modes listed above.

- All control relays shall have limit timers to prevent runaway control.

- The controller shall be able to interlock any relay output based on a digital input, or based on another specific relay being active.

Part 4.		Execution

4.1	Installation

A.	The sensors shall be installed in a location where they will always remain immersed in the sample.

- The sensors shall be installed in a location where there is good solution movement and where they will respond rapidly to changes

- The sensor cables shall be routed such that they are separated from any AC voltage by at least 6 inches.

- If the sensor cable needs to be extended beyond the standard length, then 24 AWG, 3 twisted pair, shielded cable shall be utilized.

- If the optional 4 – 20 mA output or water meter contactor are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized.

Part 5. 	Warranty

5.1 	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.		Options

6.1	Related Equipment

- Level switch or level transmitter for chemical level monitoring

- Metering pumps for chemical control

Part 7.		Spare Parts

7.1	Recommended Spare Parts

- 102834 Fuse, F1, 6 amp 250 V, 5 x 20 mm

Part 8.		Dimensions

Panel Dimensions

Part 9.		Wiring

Contacting Conductivity Sensor Input Wiring

Electrodeless Conductivity Sensor Input Wiring

pH/ORP/ISE Sensor Input Wiring

Disinfection Sensor Input Wiring

4-20mA Sensor Input Wiring

Digital Input Wiring

W600 AC Power & Relay Output Wiring

W610 AC Power & Relay Output Wiring

W620 AC Power & Relay Output Wiring

W640 AC Power & Relay Output Wiring

Analog Output Wiring