- WDC400 Series

- Boiler Condensate Conductivity Monitors

- For Two Boilers

- 180506 Rev B Revised 5/23/2012

Part 1.		General

- 1.1	Scope

A. 	This section describes the requirements for a condensate conductivity monitor for two boilers with automatically temperature compensated electrodes.

B.	Under this item, the contractor shall furnish and install the

conductivity control equipment and accessories as indicated on the plans and as herein specified.

- 1.2	Submittals

- A.	The following information shall be included in the submittal for this section:

1.	Data sheets and catalog literature for a micro-processor based condensate conductivity controller for two boilers and electrodes.

2.	Interconnection and dimensional drawings.

3.	List of spare parts

Part 2.		Products

- 2.1	Boiler condensate conductivity controller

- The boiler condensate conductivity control system shall consist of a control module that provides on/off conductivity control, alarm and two conductivity electrodes that provides measurement of the conductivity, as well as  temperature measurement for automatic compensation for errors due to temperature fluctuations.

- B.	Control Module:

- Enclosure: Polycarbonate, NEMA 4X, lockable hinged door with clear window.

- Power: 100-240 VAC, 50/60 Hz,  8A, Fuse: 1.0 ampere, 5 x 20mm

- Inputs:

- Conductivity (two): 0 to 10,000 S/cm.

- Temperature (two): Pt1000

No Flow Interlock (two): Isolated dry contact closure (reed switch)

- Outputs:

Control (on/off): Two internally powered relays, 6 A (resistive), 1/8 HP
All relays are fused together as one group, total current for this group must not exceed 6A.

4 – 20 mA (Optional): Fully isolated, internally powered, 600 ohm maximum resistive load.

- Software features:

Control relays shall feature adjustable control direction and dead band.

A self test shall be available to verify the integrity of the control module’s sensor input circuitry.

Manual activation of the relays shall be easily accomplished via the keypad.

An alarm relay shall activate on any alarm condition.

Software upgrade file shall be transferable to the controller via USB memory stick.

Optional datalog of conductivity and temperature in 10 minute increments over a two-month period.

Optional event log with time-stamped relay on/off and flow/no-flow events.

Optional configuration file import/export feature

C.	Sensors:

- Operating Principle: The conductivity sensors shall be driven with a low voltage AC signal, and the return signal voltage will vary with the conductivity of the intervening solution.

The Pt1000 temperature signals shall also be delivered to the control module, in order to automatically compensate for sensor errors due to temperature fluctuations.

- Materials of construction: 316SS, PEEK or PVDF.

- Process connections: 1” NPT Female tee with ¾” x

1” reducing bushings

- Temperature range: 0 – 200 degrees C.

- Pressure range: 0 – 250 psig.

- D.	Controller and Sensor Performance

- Range: 0 – 10,000 S/cm.

- Accuracy: From 10-10,000 S/cm ± 1% of reading; from 0-10 S/cm ± 20% of reading.

- Resolution: ± 1S/cm.

4.	Maximum separation between the controller and the

sensors shall be 250 feet.

- E.	Indication

- Graphic User Interface

A 2 line x 16 character backlit LCD display shall indicate the process value, and the status of outputs and alarms.

Five LED lamps shall indicate the on/off status of the control and alarm outputs.

- F.	Equipment

The boiler condensate conductivity controller shall be a Walchem WDC400 series.

Part 3.		Operator Functions

- 3.1	Calibration

- The conductivity electrode calibrations shall be a one point calibration, utilizing a solution of a known conductivity.

- All set points shall be set through the 8 button keypad.

- An access code shall be available to protect all set points and calibrations, while allowing the user to view any set point.

- 3.2	Control Module Function Details

- The conductivity control output shall be on/off control with adjustable dead band.

- The conductivity control direction shall be selected via the keypad.

- All control relays shall have a limit timer to prevent runaway control.

Part 4.		Execution

- 4.1	Installation

A.	The sensors shall be installed in the condensate return line between the heat exchangers and the receiver.

B.	The sensor cables shall be routed such that they are separated from any AC voltage by at least 6 inches.

C.	The sensors shall be installed in a location where they will always remain wet.

- If the sensor cables need to be extended beyond the standard 20 feet, then 24 AWG, 2 twisted pair, shielded cable shall be utilized, to a maximum of 250 ft.

- If the optional 4 – 20 mA output is installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized.

- The diverter valves shall be installed in the condensate return line between the sensor and the receiver.

Part 5.		Warranty

- 5.1	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.	Options

- 6.1	Related Equipment

- Diverter valve to prevent contaminated condensate from returning to boiler

- 100084 Sensor extension cable

Part 7.	Spare Parts

7.1	Recommended Spare Parts

- 103163 Fuse, 1 A, 250 VAC

- 102864 Fuse, 6 A, 250 VAC

| ### Measurement Performance |  | ### Mechanical |  |  |
| --- | --- | --- | --- | --- |
| Conductivity: |  | Enclosure |  | Polycarbonate |
| Range | 0-10,000 µS/cm | NEMA rating |  | NEMA 4X |
| Resolution | 1 µS/cm | Dimensions |  | See next page |
| Accuracy | 10-10,000 S/cm 1% of reading 0-10 S/cm ±20% of reading | Display |  | 2 x 16 character backlit liquid crystal |
| Temperature: |  | Ambient Temp |  | 32 to 158F (0 to 70C) |
| Range | 32 to 392F (0 to 200C) | Storage Temp. |  | -20 to 180F(-29 to 80C) |
| Resolution | 0.1° | Shipping Weight |  | 10 lbs (approximately) |
| Accuracy | 1% of reading |  |  |  |
| Inputs |  | ### Outputs |  |  |
| Power | 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 mm | Mechanical relays | 6A resistive, 1/8 HP All relays are fused together as one group, total current for this group must not exceed 6A |  |
|  |  | 4-20 mA (optional) | Fully isolated, internally powered, 600 maximum resistive load. Resolution, .001% of span, accuracy 1% of reading |  |

### Dimensions

WIRING DETAILS

A	AC POWER, 8 AMPS MAX

2 x 28 AWG PLUS GROUND OR LOCAL

CODE

B	AC POWER, 6 AMPS MAX

SOLENOID, ALARM OR METERING PUMP

2 x 18 AWG PLUS GROUND OR LOCAL

CODE

C	AC POWER, 6 AMPS MAX

MOTORIZED BALL VALVE

3 x 18 AWG PLUS GROUND OR LOCAL

CODE

D	CONDUCTIVITY ELECTRODE

4 x 24 AWG PLUS SHIELD, 20 FT SUPPLIED

E	OPTIONAL 4-20mA OUTPUT

2 x 24 AWG PLUS SHIELD

WIRING DETAILS

A	AC POWER, 8 AMPS MAX

2 x 28 AWG PLUS GROUND OR

LOCAL CODE

B	AC POWER, 6 AMPS MAX

SOLENOID, ALARM OR METERING PUMP

2 x 18 AWG PLUS GROUND OR LOCAL

CODE

C	AC POWER, 6 AMPS MAX

MOTORIZED BALL VALVE

3 x 18 AWG PLUS GROUND OR LOCAL

CODE

D	CONDUCTIVITY ELECTRODE

4 x 24 AWG PLUS SHIELD, 20 FT SUPPLIED

E	OPTIONAL 4-20mA OUTPUT

2 x 24 AWG PLUS SHIELD

WDC INSTALLATION/WIRING

Wiring Details

A	AC Power, 8 Amps maximum, 2 x 18 AWG plus ground or local code

B	AC Power, 6 Amps maximum, diverter valve, 3 x 18 AWG plus ground or local code

C	AC Power, 6 Amps maximum, alarm, 2 x 18 AWG

D	Conductivity electrode, 4 x 24 AWG & shield, 20 ft supplied

E	Optional 4-20 mA output, 2 x 24 AWG & shield

Ordering Information

VOLTAGE

OUTPUT

SENSOR      USB

WDC400-

| Voltage | Outputs | Sensor | USB |
| --- | --- | --- | --- |
| 1 = 120 VAC prewired | N = None | N = No electrode | N= Software upgrade capability only |
| 5 = 100-240 VACconduit | 4 = Single Isolated 4-20 mA | 5 = Two electrodes (up to 250 psi) | U = Integrated datalogging, event/reset logging, and configuration file import/export |
|  | 2 = Two isolated 4-20 mA |  |  |

| Agency Approvals |  |
| --- | --- |
| UL | ANSI/UL 61010-1:2004, 2nd Edition* |
| CAN/CSA | C22,2 No.61010-1:2004 2nd Edition* |
| CE Safety | EN 61010-1:2001 2nd Edition* |
| CE EMC | EN 61326-1:2006 |
| Note: For EN61000-4-6, EN61000-4-3 the controller met performance criteria B. |  |
| *Class A equipment: Equipment suitable for use in establishments other than domestic, and those directly connected to a low voltage (100-240 VAC) power supply network which supplies buildings used for domestic purposes. |  |

WDC INPUTS

WDC OUTPUTS

WDC WIRING