WDT410 Series

Bleed, Feed, pH and Dual Biocide Cooling Tower Conductivity Controllers

180509 Rev B Revised 5/23/2012

Part 1.		General

1.1	Scope

A. 	This section describes the requirements for a bleed, feed, pH and dual biocide cooling tower conductivity controller with an automatically temperature compensated electrode.

B.	Under this item, the contractor shall furnish and install the cooling tower control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the submittal for this section:

1.	Data sheets and catalog literature for a microprocessor based bleed, feed, pH and dual biocide cooling tower controller and electrode.

2.	Interconnection and dimensional drawings.

- List of spare parts

Part 2.		Products

2.1	Bleed, feed, pH and dual biocide cooling tower controller

- The bleed, feed, pH and dual biocide cooling tower control system shall consist of a control module that provides on/off conductivity control, inhibitor chemical feed, pH control, two biocide chemical feeds.  Also included shall be a pH electrode that provides measurement of the pH and a conductivity electrode that provides measurement of the conductivity, as well as a temperature measurement for automatic compensation for errors due to temperature fluctuations.

B.	Control Module:

- Enclosure: Polycarbonate, NEMA 4X, lockable hinged door with clear window.

- Power: 	100-240VAC, 50/60 Hz, 8 mA, Fuse: 1.0 Ampere, 5 x 20 mm

- Inputs:

- Conductivity: 0 to 10,000 S/cm.

- pH: 0-14 standard units

- Temperature: 10K ohm Thermistor

- No Flow Interlock: Isolated dry contact closure (reed switch)

- Water meter contactor: Isolated dry contact closure (reed switch).

- Outputs:

- Control (on/off): Five internally powered relays, 6A (resistive), 1/8 HP

- All relays are fused together as one group, total current for this group must not exceed 6A

- 4 – 20 mA (Optional): Fully isolated, internally powered, 600 ohm maximum resistive load.

- Software features:

- Conductivity and pH control relays shall feature adjustable control direction and dead band.

- Chemical feed shall be selectable from bleed and feed, feed as a percentage of bleed, feed as a percentage of time, and feed based on a water meter contactor input.

- Biocide feed shall be selectable from up to 10 times per day, a weekly cycle, a two week cycle, or a 28 day cycle.

- A self test shall be available to verify the integrity of the control module’s sensor input circuitry.

- A reminder for pH electrode calibration shall be available.

- The controller shall display an evaluation of the pH sensor’s slope versus theoretical after each two point calibration.

- Manual activation of the relays shall be easily accomplished via the keypad.

- A maximum output on-time shall be available on the bleed, pH and feed relays to prevent runaway control.

  - Software upgrade file shall be transferable to the controller via USB memory stick

  - Optional datalog of conductivity, pH, temperature and water meter totals in 10 minute increments over a two-month period

  - Optional event log with time-stamped relay on/off and flow/no-flow events

  - Optional configuration file import/export feature

C.	Sensors:

- Operating Principle: The conductivity sensor shall be driven with a low voltage AC signal, and the return signal voltage will vary with the conductivity of the intervening solution.

The pH sensor shall consist of a replaceable cartridge containing a pH sensitive glass and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

The 10K ohm temperature signal shall also be delivered to the control module, in order to automatically compensate for sensor errors due to temperature fluctuations.

- Materials of construction: Glass filled polypropylene, FKM and graphite (conductivity); CPVC, Titanium, glass, FKM (pH), PVC, glass filled polypropylene (flow switch manifold).

- Process connections: For in-line sensors, ¾” NPT Female tee.

- Temperature range: 10 – 70 degrees C.

- Pressure range: 0 – 100 psig.

D.	Controller and Sensor Performance

- Range: 	0 – 10,000 S/cm.   0-14 pH standard units.

- Accuracy:  10-10,000 S/cm ± 1% of reading;

0-10 S/cm ± 20% of reading.

0.01 pH standard units

3.	Resolution:  ± 1S/cm.

0.01 pH standard units

4.	Maximum separation between the controller and the sensors shall be 250 feet.

E.	Indication

- Graphic User Interface

- A 2 line x 16 character backlit LCD display shall indicate the process values, and the status of outputs and alarms.

- Six LED lamps shall indicate the on/off status of the control outputs.

F.	Equipment

The bleed, feed, pH and dual biocide cooling tower conductivity controller shall be a Walchem WDT410 series.

Part 3.		Operator Functions

3.1	Calibration

- The conductivity electrode calibration shall be a one point calibration, utilizing a solution of a known conductivity.

- The pH electrode calibration shall be either a one or two point calibration utilizing standard pH buffer solutions.

- All set points shall be set through the 8 button keypad.

- An access code shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- The conductivity and pH  control outputs shall be on/off control with adjustable dead band.

- The conductivity and pH control direction shall be selected via the keypad.

- The inhibitor chemical feed output shall be on/off control with four choices of feed modes.

- The bleed and feed relays shall have limit timers to prevent runaway control.

- The biocide programs shall provide a conductivity based prebleed prior to the biocide addition, and a time based lockout of the bleed after the biocide addition.

Part 4.		Execution

4.1	Installation

A.	The sensors shall be installed in a location where they will always remain immersed in the sample.

B.	The sensors shall be installed in a location where there is good solution movement and where they will respond rapidly to conductivity and pH changes.

C.	The sensor cables shall be routed such that they are separated from any AC voltage by at least 6 inches.

D.	If the conductivity sensor cable needs to be extended beyond the standard 5 feet, then 24 AWG, 2 twisted pair, shielded cable shall be utilized.

- If the pH sensor cable needs to be extended beyond the standard 5 feet, then 24 AWG, 3 twisted pair, shielded cable shall be utilized.

- If the optional 4 – 20 mA output, water meter contactor or flow switch are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized.

- The sample line shall be tapped from the discharge side of the cooling tower recirculation pump, and returned to either the cooling tower sump or the suction side of the recirculation pump.

Part 5.		Warranty

5.1	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.	Options

6.1	Related Equipment

- 191008 flow switch manifold assembly

- Solenoid valve for bleed control

- EZB16D1-VC metering pumps for chemical feed

- Water meter contactor

- 100084 sensor extension cable

- 102535 pH sensor extension cable

Part 7.	Spare Parts

7.1	Recommended Spare Parts

- 103163 Fuse, 1 A, 250VAC

- 102864 Fuse, 6 A, 250 VAC

- WEL-PHF-NN pH electrode

| ##### Measurement Performance |  | Mechanical |  |
| --- | --- | --- | --- |
| Conductivity Range | 0 - 10,000 µS/cm | Enclosure | Polycarbonate |
| Conductivity Resolution | 1 µS/cm | NEMA Rating | NEMA4X |
| Conductivity Accuracy | 10 - 10,000 µS/cm ± 1% of reading 0 – 10 µS/cm ± 20% of reading | Dimensions | See next page |
| Temperature Range | 32 to 158°F (0 to 70°C) | Display | 2 x 16 character backlit liquid crystal |
| Temperature Resolution | ± .1°C | Operating Ambient Temp. | 32 to 158°F (0 to 70°C) |
| Temperature Accuracy | ± .1% of reading | Storage Temp | -20 to 180°F (-29 to 80°C) |
| pH Range | -2 to 16 pH units | Shipping Weight | 10 lbs (approximately) |
| pH Resolution | 0.01 pH units | Graphite electrode pressure rating 100 psi |  |
| pH Accuracy (calibrated) | ±0.01 pH units |  |  |
| ORP Range | ±1500 mV | Flow switch manifold pressure rating 100 psi |  |
| ORP Resolution | 1 mV | Flow switch manifold connections ¾” NPTF |  |
| ORP Accuracy (calibrated) | ±1 mV | pH/ORP electrode pressure rating 100 psi |  |

| Inputs |  |  |  |
| --- | --- | --- | --- |
| #### Power | Controller |  | 100-240VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 10 mm |
| #### Input signals | Cond electrode |  | 1.0 cell factor, 10K thermistor |
|  | pH/ORP |  | Requires a preamplified signal. Walchem WEL series recommended. ±5V power available for external preamps. Note: Temperature compensation for pH input is accomplished using the conductivity electrode temp. element. ORP measurement does not use temp comp. |
|  | Flow meter (optional) |  | Isolated dry contact closure required (i.e., relay, reed switch, etc) |
|  | Flow switch (optional) |  | Isolated dry contact closure required (i.e., reed switch) |
| Outputs |  |  |  |
| Mechanical Relays (5) |  | WDT400: Five powered relays (Bleed & Feed for each tower, Diagnostic Alarm) WDT410: Six powered relays (Bleed, Feed, Bio 1, Bio 2, pH/ORP, Alarm) 6 A (resistive), 1/8 HP All relays are fused together as one group, total current for this group must not exceed 6A |  |
| 4-20 mA (0, 1, or 2 optional) |  | Internally powered |  |
|  |  | Fully isolated |  |
|  |  | 600ohms max resistive load |  |
|  |  | Resolution .001% of span |  |
|  |  | Accuracy ±1% of reading |  |

## Dimensions

Installation

## Ordering Information

VOLTAGE

OUTPUT

SENSOR   USB

WDT400 or 410   -

VOLTAGE					OUTPUT
1 = 120 VAC, prewired 				N = No data output

5 = 100-240 VAC, conduit				4 = Single 4-20 mA output

2 = Dual 4-20 mA output

WDT400 SENSOR
N = 	No electrode

1 = 	Two graphite electrodes & tees, (inline or submersion) 20ft. (6.1m) cable

2 = 	Two graphite electrodes & flow switch manifolds, 20 ft. (6.1m) cable

4 = 	Two high pressure electrodes & glands, 10 ft.(3m) cable
5 = 	Two high pressure electrodes & flow switch manifolds ,20 ft. (6.1m) cable

6 = 	Two SS electrodes & tees, 20 ft. (6.1m) cable

7 = 	Two SS electrode & flow switch manifolds on PP panel, 20 ft. (6.1m) cable

WDT410 SENSOR
N = 	No electrode

1 = 	SS + pH electrodes & tees, (inline or submersion), 20ft. (6.1m) cable

2 = 	SS + ORP electrodes & tees (inline or submersion),  20 ft. (6.1m) cable

3 = 	SS + pH electrodes & flow switch manifold on PP panel,  5ft. (1.5m) cable

4 = 	SS + ORP electrodes & flow switch manifold on PP panel, 5ft. (1.5m) cable

6 = 	Graphite + pH electrodes & tees (inline or  submersion), 20ft. (6.1m) cable

7= 	Graphite + ORP electrodes, & tees (inline or submersion), 20ft. (6.1m) cable

7R= 	Graphite + ORP rod style electrode & tees, ft (inline or submersion), 20ft. (6.1m) cable

8 =	Graphite + pH electrodes & flow switch manifold on PP panel,  5ft. (1.5m) cable

9 = 	Graphite + ORP rod style electrode & flow switch manifold on PP panel,  5ft. (1.5m) cable

A =	High pressure electrodes (Cond + pH) & flow switch manifold on PP panel,  5ft. (1.5m) cable

B = 	High pressure electrodes (Cond + ORP) & flow switch manifold on PP panel,  5ft. (1.5m) cable

USB FEATURES
N = Software upgrade capability only

U = Integrated datalogging, event/reset logging, and configuration file import/export

| Agency Approvals |  |
| --- | --- |
| UL | ANSI/UL 61010-1:2004, 2nd Edition* |
| CAN/CSA | C22,2 No.61010-1:2004 2nd Edition* |
| CE Safety | EN 61010-1 :2001 2nd Edition* |
| CE EMC | EN 61326-1 :2006 |
| Note: For EN61000-4-6, EN61000-4-3 the controller met performance criteria B. |  |
| *Class A equipment: Equipment suitable for use in establishments other than domestic, and those directly connected to a low voltage (100-240 VAC) power supply network which supplies buildings used for domestic purposes. |  |

# WDT410 INPUTS

# WDT410 OUTPUTS

WDT410 WIRING