WECT410 Series

Bleed, Feed and Dual Biocide Cooling Tower Conductivity Controllers with Electrodeless Conductivity Sensor

180513 Rev B Revised 5/23/2012

Part 1.		General

1.1	Scope

A. 	This section describes the requirements for a bleed, feed and dual biocide cooling tower conductivity controller with an automatically temperature compensated sensor.

B.	Under this item, the contractor shall furnish and install the

conductivity control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the submittal for this 				section:

1.	Data sheets and catalog literature for a micro-processor based bleed, feed and dual biocide cooling tower conductivity controller and sensor.

2.	Interconnection and dimensional drawings.

3.	List of spare parts

Part 2.		Products

2.1	Bleed, feed and dual biocide cooling tower conductivity controller

- The bleed, feed and dual biocide cooling tower conductivity control system shall consist of a control module that provides on/off conductivity control, inhibitor chemical feed, two biocide chemical feeds and a conductivity sensor that provides measurement of the conductivity, as well as a temperature measurement for automatic compensation for errors due to temperature fluctuations.

B.	Control Module:

- Enclosure: Polycarbonate, NEMA 4X, lockable hinged door with clear window.

2.	Power: 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 		mm

- Inputs:

- Conductivity: Two ranges: 50 to 1,000 and 1,000 to 10,000 S/cm.

- Temperature: 10 K Thermistor

- No Flow Interlock: Isolated dry contact closure (reed switch)

- Water meter contactor: Isolated dry contact closure (reed switch).

- Outputs:

  - Control (on/off): Four internally powered relays, 6 A (resistive), 1/8 HP. All relays are fused together as one group, total current for this group must not exceed 6A

  - Alarm: One internally powered relay, 10 A (resistive), 1/8 HP

  - 4 – 20 mA (Optional): Fully isolated, internally powered, 600 ohm maximum resistive load.

- Software features:

  - Control relay shall feature adjustable control direction and dead band.

  - Chemical feed shall be selectable from bleed and feed, feed as a percentage of bleed, feed as a percentage of time, feed based on a water meter contactor input, and feed based on a paddlewheel flowmeter input.

  - Biocide feed shall be selectable from up to 10 times per day, a weekly cycle, a two week cycle, or a 28 day cycle.

  - A self test shall be available to verify the integrity of the control module’s sensor input circuitry.

  - Manual activation of the relays shall be easily accomplished via the keypad.

  - A maximum output on-time shall be available on the bleed and feed relays to prevent runaway control.

  - Software upgrade file shall be transferable to the controller via USB memory stick

  - Optional datalog of conductivity, temperature and water meter totals in 10 minute increments over a two-month period

  - Optional event log with time-stamped relay on/off and flow/no-flow events

  - Optional configuration file import/export feature

C.	Sensor:

- Operating Principle: The conductivity sensor shall be driven with a low voltage signal, and the return signal voltage will vary with the conductivity of the intervening solution.

The 10 K ohm temperature signal shall also be delivered to the control module, in order to automatically compensate for sensor errors due to temperature fluctuations.

- Materials of construction: CPVC, Glass filled polypropylene, FKM.

- Process connections: For in-line sensors, ¾” NPT Female.

- Temperature range: 0 – 60 degrees C.

- Pressure range: 0 – 150 psig.

D.	Controller and Sensor Performance

- Range: Two ranges: 1000 – 10,000 S/cm and 50 – 1,000 S/cm.

- Accuracy: Within range  ± 1% of reading; Outside range ± 20% of reading.

- Resolution: ± 1S/cm.

4.	Maximum separation between the controller and the

sensor shall be 250 feet.

E.	Indication

- Graphic User Interface

A 2 line x 16 character backlit LCD display shall indicate the process value, a bar graph of the process value relative to set points, and the status of outputs and alarms.

Five LED lamps shall indicate the on/off status of the relay outputs.

F.	Equipment

The bleed, feed and dual biocide cooling tower conductivity controller shall be a Walchem WECT410 series.

Part 3.		Operator Functions

3.1	Calibration

- The conductivity sensor calibration shall consist of a zero calibration plus a one point process calibration, utilizing a solution of a known conductivity.

- All set points shall be set through the 8 button keypad.

- An access code shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- The conductivity control output shall be on/off control with adjustable dead band.

- The conductivity control direction shall be selected via the keypad.

- The inhibitor chemical feed output shall be on/off control with five choices of feed modes.

- The bleed and feed relays shall have limit timers to prevent runaway control.

- The biocide programs shall provide a conductivity based prebleed prior to the biocide addition, and a time based lockout of the bleed after the biocide addition.

Part 4.		Execution

4.1	Installation

A.	The sensor shall be installed in a location where it will always remain immersed in the sample.

B.	The sensor shall be installed in a location where there is good solution movement and where it will respond rapidly to conductivity changes.

C.	The sensor cable shall be routed such that it is separated

from any AC voltage by at least 6 inches.

D.	If the sensor cable needs to be extended beyond the standard 5 feet, then 24 AWG, 3 twisted pair, shielded cable shall be utilized.

- If the optional 4 – 20 mA output, water meter contactor or flow switch are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized.

- The sample line shall be tapped from the discharge side of the cooling tower recirculation pump, and returned to either the cooling tower sump or the suction side of the recirculation pump.

Part 5.		Warranty

5.1	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.	Options

6.1	Related Equipment

- 191022 flow switch manifold assembly

- Solenoid valve for bleed control

- EHB16R1-VC metering pumps for chemical feed

- Water meter contactor

- 102535 Sensor extension cable

Part 7.	Spare Parts

7.1	Recommended Spare Parts

- 103163 Fuse, 1 A, 250 VAC

- 102834 Fuse, 6 A, 250 VAC

| Measurement Performance |  | Mechanical |  |
| --- | --- | --- | --- |
| Conductivity Ranges | 1,000-10,000 S/cm 50-1,000 S/cm | Enclosure | Polycarbonate |
| Resolution | 1 S/cm | NEMA rating | NEMA 4X standard |
| Accuracy | Within range  1% of reading Outside range 20% of reading | Dimensions | See below |
|  |  | Display | 2 x 16 character backlit liquid crystal |
| Temperature Range | 32-158F (0 to 70C) | Ambient Temp. | 32-158F (0-70C) |
| Resolution | 0.1 degree | Shipping wgt. | 10 lbs (approximately) |
| Accuracy | 1% of reading |  |  |
| Inputs |  | Outputs |  |
| Power | 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 mm | Mechanical Relays | Five powered relays 6A resistive, 1/8 HP All relays are fused together as one group, total current for this group must not exceed 6A |
| Signals | (Optional) Flow Meter-isolated, dry contact closure required (relay reed switch) (Optional) Flow Switch-isolate, dry contact closure required (reed switch) | 4-20mA(Optional) | Fully isolated, internally powered600 max. resistive load. Resolution 0.001% of span, accuracy 1% of reading |

## Dimensions

Installation

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | AC POWER, 6 AMPS MAXIMUM, SOLENOID, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| C | AC POWER, 6 AMPS MAXIMUM, METERING PUMP, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| D | CONDUCTIVITY SENSOR, 6 x 24 AWG PLUS SHIELD, 5 FT SUPPLIED |
| E | FLOW SWITCH, 2 x 24 AWG PLUS SHIELD, 5 FT SUPPLIED |
| F | OPTIONAL WATER METER, 2 x 24 AWG PLUS SHIELD |
| G | OPTIONAL 4-20mA OUTPUT, 2 X 24 AWG PLUS SHIELD |
| H | AC POWER, 6 AMPS MAXIMUM, ALARM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |

## WECT Series, Bleed & Feed Controller with Biocide Additions

## Ordering Information

VOLTAGE

OUTPUT

SENSOR   USB

WECT410   -

VOLTAGE
1 = 120 VAC, prewired

5 = 100-240 VAC, hardwired, cable glands

OUTPUT
N = No data output

4 = Isolated 4-20 mA output

SENSOR
N = No electrodeless conductivity sensor

1 = Electrodeless sensor and tee, 20 ft cable (for inline mounting)

2 = Electrodeless sensor & flow switch manifold on PP panel, 5 ft cable

2L = Electrodeless sensor & flow switch manifold (loose - no panel), 20 ft cable

3 = Submersion sensor (no tee or adaptor), 20 ft cable

USB FEATURES
N = Software upgrade capability only

U = Integrated datalogging, event/reset logging, and  configuration file import/export

Safety Approvals

| Agency Approvals |  |
| --- | --- |
| UL | ANSI/UL 61010-1:2004, 2nd Edition* |
| CAN/CSA | C22,2 No.61010-1:2004 2nd Edition* |
| CE Safety | EN 61010-1:2001 2nd Edition* |
| CE EMC | EN 61326-1:2006 |
| Note: For EN61000-4-6, EN61000-4-3 the controller met performance criteria B. |  |
| *Class A equipment: Equipment suitable for use in establishments other than domestic, and those directly connected to a low voltage (100-240 VAC) power supply network which supplies buildings used for domestic purposes. |  |

# WECT400/410 INPUTS

# WECT410 OUTPUTS

# WECT410 Conduit Wiring