WMT8000 Series

WebMaster Multi I/O Cooling Tower Controllers

Part 1.		General

1.1	Scope

A.	This section describes the requirements for a multiple input/output cooling tower controller.

B.	Under this item, the contractor shall furnish and install the

Multi I/O cooling tower control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the 				submittal for this section:

1.	Data sheets and catalog literature for the WebMaster multi I/O cooling tower controller and sensors.

2.	Interconnection and dimensional drawings.

3.	List of spare parts

Part 2.		Products

2.1	Multi I/O cooling tower controller

A.	The multi I/O cooling tower control system shall be a capable of measuring system conductivity, makeup conductivity, pH, ORP, and temperature. The conductivity sensors shall be either a contacting style or an electrodeless style. All sensors shall have integral signal conditioning. Additional inputs shall include a flow switch, two water meter inputs, eight optional 4-20 mA inputs and six optional digital inputs. Outputs shall include eight mechanical relays, and four optional 4-20 mA outputs. Digital communications shall be via USB, Ethernet, and/or optional modem. Up to 16 controllers may be networked together over Ethernet. Integration with DCS, SCADA system or building energy management systems shall be possible using the optional Modbus TCP/IP feature. The controller shall be accessible via the Internet for configuring, data logging, and control of relay outputs. The controller shall provide notification of alarm conditions via dry contact closure, pager, and/or email.

B.	Control Module:

- Enclosure: Fiberglass, NEMA 4X, lockable hinged door with clear window.

2.	Power:		100-240 VAC  10%, 50/60 Hz

3.	Inputs:

Input signals STANDARD

Water meter Contactor: Isolated dry contact (relay, reed switch or Hall Effect) 0-10 Hz, 50 msec minimum width

Paddlewheel Water Meter: Isolated dry contact (relay, reed switch or Hall Effect) 0-300 Hz, 1.5 msec minimum width

Flow switch: Isolated dry contact (relay, reed switch or Hall Effect) 0-10 Hz, 50 msec minimum width

Input signals OPTIONAL

Digital Inputs (1-4) Isolated dry contact (relay, reed switch or Hall Effect) 0-10 Hz, 50 msec minimum width

Digital Inputs (5-6) Isolated dry contact (relay, reed switch or Hall Effect) 0-300 Hz, 1.5 msec minimum width

Point Level Switch: Isolated dry contact (relay, reed switch or Hall Effect)

Flow Feedback: Isolated dry contact (relay, reed switch or Hall Effect)

Analog Inputs (1-8) 4-20 mA: 2-wire or 3 -wire, internally powered by 24 VDC, 25 ohm input resistance, 1000 ohm maximum load.

Sensor STANDARD (1) Signal (isolated) ±1.5V, Temp (isolated) 1K or 10K or 100K Temp

Sensor OPTIONAL (3)  Signal (isolated) ±1.5V (isolated) 1K or 10K or 100K

- Outputs:

STANDARD

Mechanical relays: At 115 VAC, 10 amp (resistive), 1/8 HP

At 230 VAC, 6 amp (resistive), 1/8 HP

R1-R4 are fused together as one group, total current not to exceed 5.5A

R5-R8 are fused together as one group, total current not to exceed 5.5A

Relays may switch mains voltage or may be dry contact, according to model number. Powered relays have NO and NC terminals available. Only powered relays are fused.

Digital: USB, Ethernet 10 Base T

OPTIONAL

4-20 mA (1-4): Isolated, 500 ohm maximum resistive load, internally powered

5.	Software features:

Conductivity, ORP and pH control relays shall feature adjustable control direction and dead band.

Chemical feed shall be selectable from bleed and feed, feed as a percentage of bleed, feed as a percentage of time, and feed based on a water meter contactor input.

Biocide feed shall be selectable from up to 10 times per day, a weekly cycle, a two week cycle, or a 28 day cycle.

Conductivity control may be based on a direct sensor signal, a 4-20 mA input, or cycles of concentration.  pH control may be based on a direct sensor signal or a 4-20 mA input signal. ORP control may be based on a direct sensor signal, based on a 4-20 mA input signal, or based on a direct sensor signal with an occasional higher set point on a timed basis.

Control of a cooling tower, boiler, closed loop, or process shall be possible using a single controller.

A self test shall be available to verify the integrity of the control module’s sensor input circuitry.

A reminder for electrode calibration shall be available.

The controller shall display an evaluation of the pH sensor’s slope versus theoretical after each two point calibration.

Manual activation of the relays shall be easily accomplished via the keypad, or a PC.

A maximum output on-time shall be available on the control relays to prevent runaway control.

Any relay may be reconfigured to any one of a number of control algorithms, responding to the signal from any input desired.

The optional analog inputs shall be configurable for level sensors, corrosion monitors, or any other type of transmitter, providing appropriate units of measure and scaling.

The optional digital inputs shall be configurable for level switches, chemical feed verification switches or generic interlock operation.

Status reports and data files shall be sent automatically via email on either a cyclical basis or for a specific date range.

The controller set points may be entered by downloading them from one controller, and uploading them into another controller.

Access to the controller shall be possible using an USB connection, Ethernet, direct modem-to-modem, via the Internet, or via the local display and keypad, simultaneously if desired.

No proprietary software shall be required on the user’s computer to communicate with the controller, or to view or change set points.

The controller software shall be able to be upgraded remotely via the Internet.

C.	Sensors:

Contacting Conductivity

1.	Operating principle: The conductivity sensor shall be driven with a low voltage AC signal, and the return signal voltage will vary with the conductivity of the intervening solution. The temperature sensor within this sensor compensates for the effect of temperature on the conductivity signal.

2.	Materials of construction: Glass-Filled Polypropylene, Graphite, FKM

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-150 psi

- Other materials and higher pressure sensors shall be made available.

Electrodeless Conductivity

1.	Operating principle: The conductivity sensor shall be driven with a low voltage AC signal, which induces a current in the surrounding liquid which varies in intensity with the conductivity of the liquid, which is picked up by the sensor and transmitted to the controller. The temperature sensor within this sensor compensates for the effect of temperature on the conductivity signal.

2.	Materials of construction: CPVC, FKM

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-150 psi

pH

1.	Operating principle: The pH sensor shall consist of a replaceable cartridge containing a pH sensitive glass and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module. The temperature signal from the conductivity sensor shall be used to compensate the pH reading as well.

2.	Materials of construction: Glass-Filled Polypropylene, CPVC, HDPE, FKM, Glass

3.	Process connections: ¾” NPTF

4.	Temperature range: 50-158 F, 10-70 C

- Pressure range: 0-100 psi

- Other materials and higher pressure sensors shall be made available.

ORP

1.	Operating principle: The ORP sensor shall consist of a replaceable cartridge containing a platinum electrode and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

2.	Materials of construction: Glass-Filled Polypropylene, CPVC, HDPE, FKM, Glass, and Platinum.

3.	Process connections: ¾” NPTF

4.	Temperature range: 32-158 F, 0-70 C

- Pressure range: 0-100 psi

- Other materials and higher pressure sensors shall be made available.

D.	Controller and Sensor Performance

1.	Range: 0 to 10,000 S/cm conductivity, -2 to 16 pH, -1000 to 1000 mV ORP

2.	Accuracy:  1 S/cm conductivity,  0.01 pH,  1 mV ORP

3.	Resolution: 1 S/cm conductivity, 0.01 pH, 1 mV ORP

4.	Maximum separation between controller and sensor shall be 1000 feet for pH and ORP, 250 feet for conductivity.

E.	Indication

1.	Graphic User Interface

A 64 x 128 Pixel Backlit LCD Graphics Module display shall indicate the process values, and the status of outputs and alarms.

Eight LED lamps shall indicate the on/off status of the control outputs.

F.	Equipment

The multi I/O cooling tower controller shall be a Walchem WebMaster WMT8000 series.

Part 3.		Operator Functions

3.1	Calibration

- The contacting conductivity electrode calibration shall be a one point process calibration. The electrodeless conductivity sensor calibration shall be a two point calibration (in air and at the process value), or a one point process calibration.

- The pH electrode calibration shall be either a one or two point calibration utilizing standard pH buffer solutions or a single point process calibration.

- The ORP electrode calibration shall be either a one or two point calibration utilizing standard solutions or a single point process calibration.

- All set points shall be set through the 12 button keypad, or via a PC connected either locally via USB or Ethernet, or remotely via modem or Ethernet.

- Three levels of access codes shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- The conductivity, pH, and ORP control outputs shall be on/off control with adjustable dead band.

- The conductivity, pH and ORP control directions shall be selectable.

- The inhibitor chemical feed output shall be on/off control with four choices of feed modes.

- All control relays shall have limit timers to prevent runaway control.

- The biocide programs shall provide a conductivity-based or a time-based prebleed prior to the biocide addition, and a time-based lockout of the bleed after the biocide addition.

- A dispersant, surfactant or penetrant may be added, either before or after the biocide add.

- The controller shall be able to interlock any relay output based on a digital input, or based on another specific relay being active.

Part 4.		Execution

4.1	Installation

A.	The sensors shall be installed in a location where they will always remain immersed in the sample.

- The sensors shall be installed in a location where there is good solution movement and where they will respond rapidly to changes

- The sensor cables shall be routed such that they are separated from any AC voltage by at least 6 inches.

- If the sensor cable needs to be extended beyond the standard length, then 24 AWG, 3 twisted pair, shielded cable shall be utilized.

- If the optional 4 – 20 mA output or water meter contactor are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized.

- The sample line shall be tapped from the discharge side of the cooling tower recirculation pump, and returned to either the cooling tower sump or the suction side of the recirculation pump.

Part 5. 	Warranty

5.1 	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.		Options

6.1	Related Equipment

- Solenoid valve for bleed control

- Water meter for makeup and/or bleed flow

- Level switch or level transmitter for chemical level monitoring

- Metering pumps for chemical control

Part 7.		Spare Parts

7.1	Recommended Spare Parts

- 102833 Fuse, F1, 1.6 amp

- 102834 Fuse, F2 and F3, 6.3 amp

- WEL-PHF-NN Electrode, pH

- WEL-MVR-NN Electrode, ORP, rod style