WDP410/420/440 Series

Wall Mount Dual Input pH/ORP Controllers

180518 Rev B Revised 5/23/2012

Part 1.		General

1.1	Scope

A. 	This section describes the requirements for a dual input pH/ORP controller with automatically temperature compensated electrodes.

B.	Under this item, the contractor shall furnish and install the dual input pH/ORP control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the submittal for this section:

1.	Data sheets and catalog literature for a micro-processor based dual input pH/ORP controller and electrodes.

2.	Interconnection and dimensional drawings.

3.	List of spare parts

##### Part 2.		Products

2.1	Wall Mount Dual Input pH/ORP Controller

- The wall mount pH/ORP control system shall consist of a control module that provides either on/off or pulse proportional control, one or two pH electrode(s) that provides a differential measurement of the pH, as well as a temperature measurement for automatic compensation for errors due to temperature fluctuations, or one or two ORP electrode(s) that provide a differential measurement of the ORP.

B.	Control Module:

- Enclosure: Polycarbonate, NEMA 4X, lockable hinged door with clear window.

2.	Power: 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 mm

3.	Inputs:

- pH/ORP (two): ± 1500 mV, preamplified

- Temperature (two): Pt1000 or Pt100 (pH only)

- Interlock (two): Isolated dry contact closure (flow or level switch)

- Outputs:

  - WDP410

Control 1-4 and Alarm: Internally powered relays, 6 A (resistive), 1/8 HP.

- WDP420

Control 1&2: Opto-isolated solid state relay, 150 mA, 40 VDC maximum

Control 3&4 + alarm: Dry contact relays, 6 A (resistive), 1/8 HP

- WDP440

Control 1-4: Opto-isolated solid state relay, 150 mA, 40 VDC maximum

Alarm: Dry contact relay, 6 A (resistive), 1/8 HP.

4 – 20 mA (One or two optional): Fully isolated, internally powered, 600 ohm maximum resistive load.

Power to preamplifier: +/- 5 VDC

- Software features:

- The presence of a pH or ORP electrode attached to each input shall be selectable.

- Relays shall be configurable as high or low control, high alarm, low alarm, out of range alarm, in range output, or probe wash.

- Control relays shall feature a programmable maximum on time, adjustable control direction and dead band.

- Pulse proportional control outputs shall feature a programmable maximum on time, adjustable control direction, proportional band, and both minimum and maximum pump stroke rates.

- A self test shall be available to verify the integrity of the control module’s sensor input circuitry.

- The controller shall display an evaluation of the sensor’s slope versus theoretical after each two point calibration.

- Manual activation of the relays shall be easily accomplished via the keypad.

- Software upgrade file shall be transferable to the controller via USB memory stick.

- Optional datalog of conductivity, temperature and water meter totals in 10 minute increments over a two-month period.

- Optional event log with time-stamped relay on/off and flow/no-flow events.

- Optional configuration file import/export feature

C.	Sensors:

- Operating Principle: The pH sensor shall consist of a replaceable cartridge containing a pH sensitive glass and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

The Pt1000 or Pt100 temperature signal shall also be delivered to the control module, in order to automatically compensate for sensor errors due to temperature fluctuations in pH applications.

The ORP sensor shall consist of a replaceable cartridge containing an ORP sensitive platinum rod and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

- Materials of construction:

pH: CPVC, FKM, Glass, and High Density Polyethylene.

ORP: CPVC, FKM, Platinum, Glass, and High Density Polyethylene

In line tee: Glass filled polypropylene

Flow switch: Glass filled polypropylene and PVC

- Process connections: For submersible sensors, 1” NPT Male. For in-line sensors, 1 ¼” NPT Male or G 1 ¼ adapters, or ¾” NPTF polypropylene tee

- Temperature range: 10 – 70 degrees C.

- Pressure range: 0 – 100 psig.

- Power: ± 5 VDC, 5 mA.

D.	Controller and Sensor Performance

- Range: -2 to 16 pH units, ± 1500 mV

- Accuracy: ± 0.01 pH units, ± 1 mV (as calibrated).

- Resolution: ± 0.0015 pH units (0.01 displayed), ± 1 mV.

4.	Maximum separation between the controller and the sensor shall be 1000 feet.

E.	Indication

- Graphic User Interface

A 2 line x 16 character backlit LCD display shall indicate the process values, and the status of outputs and alarms.

Five LED lamps shall indicate the on/off status of the relay outputs.

F.	Equipment

The wall mount pH controller shall be a Walchem WPH410, 420, or 440 series with WEL series pH electrodes.

Part 3.		Operator Functions

3.1	Calibration

- The pH electrode calibration shall be either a two point, or a one point calibration, utilizing buffer solutions of a known pH. Automatic recognition of standard buffer solutions shall be available.

- The ORP electrode calibration shall be either a two point, or one point calibration, using buffer solutions of a known ORP.

- The controller shall evaluate the pH electrode slope versus theoretical slope after each two point calibration.

- All set points shall be set through the 8 button keypad.

- An access code shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- The relay outputs shall be either on/off control with adjustable dead band, or time proportional control with an adjustable proportional band and time period, or configurable as a low alarm, high alarm, in range output, out of range alarm or a probe wash output.

- The pulse outputs shall offer a set point, adjustable proportional band and minimum and maximum pump stroke rate settings.

- The probe wash output feature shall provide a dry contact closure up to 10 times per day, for a programmable amount of time, while ignoring the pH/ORP reading for control purposes for a programmable amount of time.

Part 4.		Execution

4.1	Installation

A.	The pH or ORP sensors shall be installed in a location where they will always remain immersed in the sample.

- The pH or ORP sensors shall be installed in a vertical orientation, with the measuring surfaces pointing down.

C.	The pH or ORP sensors shall be installed in a location where there is good solution movement and where they will respond rapidly to chemical additions.

D.	The pH or ORP sensor cables shall be routed such that they are separated from any AC voltage by at least 6 inches.

- If the sensor cables need to be extended beyond the standard 20 feet, then 24 AWG, 3 twisted pair, shielded cable shall be utilized, to a maximum distance of 1000 feet.

- If the optional 4 – 20 mA outputs or flow switches are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized, to a maximum distance of 3000 feet.

Part 5.		Warranty

5.1	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.	Options

6.1	Related Equipment

- 190851 Junction box for sensor cable extension.

- 102535 Sensor extension cable, 24 AWG, 3 twisted pair, shielded.

- 191005 Flow switch manifold for in-line applications with two sensors in a single sample stream.

- 191006 Flow switch manifold for in-line applications with sensors in separate sample streams.

- Calibration buffers (pH 4, 7 and 10).

- ORP calibration kit

Part 7.	Spare Parts

7.1	Recommended Spare Parts

- 103163 Fuse, 1 A, 250 VAC

- 102864 Fuse, 6 A, 250 VAC

- WEL-PHF-NN pH electrode cartridge

- WEL-MVF-NN ORP electrode cartridge

| ##### Measurement Performance |  | ##### Mechanical |  |
| --- | --- | --- | --- |
| Range | -2 to 16 pH ± 1500 mV (ORP) | Enclosure | Polycarbonate |
| Resolution | .0015 pH units (0.01 pH displayed) 92 µV (1 mV displayed) (ORP) | NEMA Rating | NEMA4X |
| Accuracy (Calibrated) | ± .01 pH ±1 mV (ORP) | Dimensions | 8.5 x 6.5 x 5.5 |
| Temp. Comp. (optional) | 100 or 1000 ohm platinum RTD | Display | 2 x 16 character backlit liquid crystal |
| Temperature Range | 32 to 212°F (0 to 100°C) | Operating Ambient Temp. | 32 to 122°F (0 to 50°C) |
| Temperature Resolution | ± .09°F (.05°C) | Storage Temp | -20 to 180°F (-29 to 180°C) |
| Temperature Accuracy | ± .9°F (.5°C) | Shipping Weight | 7 lbs (approx) |
|  |  | Flow Switch Manifold Assembly | Temp 140°F (60°C) max Pressure 100 psi max Process connectors ¾” NPTF |

| ##### Inputs |  |  |  |
| --- | --- | --- | --- |
| #### Power | Controller |  | 100-240 VAC, 50/60 Hz, 8A |
| #### Input signals (two of each type are available) | pH/ORP |  | ±1500 mV |
|  | Temp Comp (optional) |  | Pt1000 or Pt100 |
|  | Interlock (optional) |  | Isolated dry contact closure required (i.e., flow, level, etc) |
| Note: A preamplified electrode signal is required. The WEL electrode has preamp built in; the controller also accepts external preamplifiers. |  |  |  |
| ##### Outputs |  |  |  |
| WDP410 (ON/OFF Control version) |  | WDP420 (Proportional version) |  |
| Control 1-4 and Diagnostic Alarm |  | Control 1-2 |  |
| Internally powered relays |  | Solid state relays |  |
| 6A resistive, 1/8 hp |  | 150 mA, 40 VDC max. |  |
|  |  | VLOWMAX = .13V @ 18 mA |  |
|  |  | Control 3-4 and Alarm |  |
|  |  | Dry contact relays |  |
|  |  | 6A resistive, 1/8 hp |  |

| WDP440 (Dual Proportional Control version) | All models (4-20mA, one or two optional) |
| --- | --- |
| Control 1- 4 | Fully isolated, internally powered, 600 max. resistive load. Resolution .001% of span, accuracy ±1% of reading |
| Solid state relays |  |
| 150 mA, 40 VDC max | ## External preamp power |
| VLOWMAX = .13V @ 18 mA | ±5VDC, 5 mA available (supplied by controller) |
| Diagnostic Alarm Relay | ## Junction Box |
| Dry contact relay | If more than 9 devices will be connected (any combination of sensors, flow/level switches, control devices, chart recorders and alarms) a junction box should be ordered (P/N 190851). |
| 6A resistive, 1/8 hp |  |

### Safety Approvals

| Agency Approvals |  |
| --- | --- |
| UL | ANSI/UL 61010-1:2004, 2nd Edition* |
| CAN/CSA | C22,2 No.61010-1:2004 2nd Edition* |
| CE Safety | EN 61010-1:2001 2nd Edition * |
| CE EMC | EN 61326-1:2006 |
| Note: For EN61000-4-6, EN61000-4-3 the controller met performance criteria B. |  |
| *Class A equipment: Equipment suitable for use in establishments other than domestic, and those directly connected to a low voltage (100-240 VAC) power supply network which supplies buildings used for domestic purposes. |  |

Dimensions

###### Installation – WDP410 In-Line Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | AC POWER, 6 AMPS MAXIMUM, METERING PUMP, ALARM 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL FLOW SWITCH, 2 x 24 AWG + SHIELD, 3 FT SUPPLIED |
| E | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |

Installation – WDP420 In-Line Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200mA MAXIMUM, METERING PUMP, 2 x 22 AWG + SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL FLOW SWITCH, 2 x 24 AWG + SHIELD, 3 FT SUPPLIED |
| E | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |
| F | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

Installation – WDP440 In-Line Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200mA MAXIMUM, METERING PUMP, 2 x 22 AWG + SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL FLOW SWITCH, 2 x 24 AWG + SHIELD, 3 FT SUPPLIED |
| E | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |
| F | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

Installation – WDP410 Submersion Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | AC POWER, 6 AMPS MAXIMUM, METERING PUMP OR ALARM , 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |

Installation – WDP420 Submersion Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200mA MAXIMUM, METERING PUMP, 2 x 22 AWG + SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |
| E | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

Installation – WDP440 Submersion Mounting

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200mA MAXIMUM, METERING PUMP, 2 x 22 AWG + SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG + SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG + SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL 4-20 mA OUTPUT, 2 x 24 AWG + SHIELD |
| E | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

## WDP Series Ordering Information

WDP410/420/440  Controller

# WDP4		    0  -

CONTROL

DATA

VOLTAGE

OPTIONS

| PART # / CODE | DESCRIPTION |
| --- | --- |
| WDP410 | pH/ORP Controller, with 4 on/off control outputs and diagnostic alarm relay |
| WDP420 | pH/ORP Controller, w/ 2 pulse proportional and 2 on/off control outputs and diagnostic alarm relay |
| WDP440 | pH/ORP Controller, with 4 pulse proportional control outputs and diagnostic alarm relay |
| voltage |  |
| 1 | 115 VAC, pre-wired with 6” pigtails (if on/off) or with 10’ cables for E-Class pumps (if pulse) |
| 5 | Hardwired, cable glands |
| Note: To connect 10 ft. cables from WDP420/440 to EW pumps, order one E90495 connector per pump. |  |
| data output |  |
| N | No 4-20 mA output |
| 4 | Single isolated 4-20 mA output |
| 2 | Dual 4-20 mA output |
| sensor options |  |
| N | No electrode |
| 2 | Two submersion flat pH electrodes without Auto Temp Comp |
| 5 | Two submersion ORP electrodes |
| 6 | One each submersion flat pH and ORP electrodes without Auto Temp Comp |
| 7 | One each in-line flat pH & ORP electrodes w/out Auto Temp Comp - includes 3/4” NPTF tees |
| 7R | One each in-line flat pH & rod style ORP electrodes w/out Auto Temp Comp includes 3/4” NPTF tees |
| 8 | One each in-line flat pH and ORP electrodes, without Auto Temp Comp plus flow switch (both electrodes mounted in same sample stream) on panel |
| 8R | One each in-line flat pH and rod style ORP electrodes, without Auto Temp Comp plus flow switch (both electrodes mounted in same sample stream) on panel |
| 8T | One each in-line flat pH and ORP electrodes, with Auto Temp Comp plus flow switch (both electrodes mounted in same sample stream) on panel |
| usb |  |
| N | Software upgrade capability only |
| U | Integrated datalogging and config file import/export via USB flash stick |

NOTE: See the WEL Series pH/ORP Electrode prices for additional electrode options, such as bulb style pH, HF resistant pH, housings that provide automatic temperature compensation (ATC), and metric in-line mounting. To order: Order the WDP controller with the option “N”, then order the appropriate WEL electrode. Make sure to specify either WEL housing option 1 or 2, which contain a preamplifier.

# WDP410 Conduit Wiring

WDP 420 Conduit Wiring

### WDP 440 Conduit Wiring

### WDP Inputs using WEL pH/ORP Electrode Housings

WDP Inputs using pH/ORP Electrode/External Preamplifiers

WDP410 Outputs

WDP420 Outputs

WDP440 Outputs