WPH410/420 Series

Wall Mount pH Controllers

180516 Rev B Revised 5/23/2012

## Part 1.	General

1.1	Scope

A. 	This section describes the requirements for a pH controller with an automatically temperature compensated electrode.

B.	Under this item, the contractor shall furnish and install the pH control equipment and accessories as indicated on the plans and as herein specified.

1.2	Submittals

A.	The following information shall be included in the submittal for this section:

1.	Data sheets and catalog literature for a micro-processor based pH controller and electrode.

2.	Interconnection and dimensional drawings.

- List of spare parts

Part 2.	Products

2.1	Wall Mount pH Controller

- The wall mount pH control system shall consist of a control module that provides either on/off or pulse proportional control, and a pH electrode that provides a differential measurement of the pH, as well as a temperature measurement for automatic compensation for errors due to temperature fluctuations.

B.	Control Module:

- Enclosure: Polycarbonate, NEMA 4X, lockable hinged door with clear window.

- Power: 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 mm

- Inputs:

  - pH: ± 1500 mV, preamplified

  - Temperature: Pt100 or Pt1000

  - Interlock: Isolated dry contact closure (flow or level switch)

- Outputs:

  - Control 1 & 2 (on/off): Internally powered relays, 6 A (resistive), 1/8 HP

  - Control 1 & 2 (proportional): Opto-isolated open collector, 50 mA, 20 VDC maximum

  - Control 3, 4 & Alarm: Dry contact relays, 6 A (resistive), 1/8 HP.

  - 4 – 20 mA (Optional): Fully isolated, internally powered, 600 ohm maximum resistive load.

- Software features:

  - Control relays shall feature adjustable control direction and dead band.

  - Pulse proportional control outputs shall feature adjustable control direction, proportional band, and both minimum and maximum pump stroke rates.

  - Auxiliary relays shall  be configurable as high alarm, low alarm, out of range alarm, in range output, or probe wash.

  - A self test shall be available to verify the integrity of the control mThe controller shall display an evaluation of the sensor’s slope versus theoretical after each two point calibration.

  - Manual activation of the relays shall be easily accomplished via the keypad.

  - A maximum output on-time shall be available to prevent runaway control.

  - Software upgrade file shall be transferable to the controller via USB memory stick.

  - Optional datalog of conductivity, temperature and water meter totals in 10 minute increments over a two-month period.

  - Optional event log with time-stamped relay on/off and flow/no-flow events.

  - Optional configuration file import/export feature

C.	Sensor:

- Operating Principle: The sensor shall consist of a replaceable cartridge containing a pH sensitive glass and silver/silver chloride reference. Voltage signals from these shall be measured against the solution ground, and the differential voltage measurement sent to the control module.

The Pt100 or Pt1000 temperature signal shall also be delivered to the control module, in order to automatically compensate for sensor errors due to temperature fluctuations.

- Materials of construction: CPVC, FKM, PP, Glass, and High Density Polyethylene.

- Process connections: For submersible sensors, 1” NPT Male. For in-line sensors, 1 ¼” NPT Male or G 1 ¼ adapters, or ¾” NPTF polypropylene tee.

- Temperature range: 10 – 70 degrees C.

- Pressure range: 0 – 100 psig.

- Power: ± 5 VDC, 5 mA.

D.	Controller and Sensor Performance

- Range: -2 to 16 pH units.

- Accuracy: ± 0.01 pH units (as calibrated).

- Resolution: ± 0.0015 pH units (0.01 displayed).

4.	Maximum separation between the controller and the sensor shall be 1000 feet.

E.		Indication

- Graphic User Interface

A 2 line x 16 character backlit LCD display shall indicate the process value, a bar graph of the process value relative to set points, and the status of outputs and alarms.

2.	Five LED lamps shall indicate the on/off status of the relay outputs.

F.	Equipment

The wall mount pH controller shall be a Walchem WPH 410 or 420 series with a WEL series pH electrode.

Part 3.	Operator Functions

3.1	Calibration

- The pH electrode calibration shall be either a two point, or a one point calibration, utilizing buffer solutions of a known pH. Automatic recognition of standard buffer solutions shall be available.

- The controller shall evaluate the electrode slope versus theoretical slope after each two point calibration.

- All set points shall be set through the 8 button keypad.

- An access code shall be available to protect all set points and calibrations, while allowing the user to view any set point.

3.2	Control Module Function Details

- The relay outputs shall be either on/off control with adjustable dead band, or time proportional control with an adjustable proportional band and time period, or configurable as a low alarm, high alarm, in range output, out of range alarm or a probe wash output.

- The pulse outputs shall offer a set point, adjustable proportional band and minimum and maximum pump stroke rate settings.

- The probe wash output feature shall provide relay activation up to 10 times per day, for a programmable amount of time, while ignoring the pH reading for control purposes for a programmable amount of time.

Part 4.	Execution

4.1	Installation

A.	The pH sensor shall be installed in a location where it will always remain immersed in the sample.

- The pH sensor shall be installed in a vertical orientation, with the measuring surface pointing down.

C.	The pH sensor shall be installed in a location where there is good solution movement and where it will respond rapidly to chemical additions.

D.	The pH sensor cable shall be routed such that it is separated from any AC voltage by at least 6 inches.

- If the sensor cable needs to be extended beyond the standard 10 feet, then 24 AWG, 3 twisted pair, shielded cable shall be utilized, to a maximum distance of 1000 feet.

- If the optional 4 – 20 mA output or flow switch are installed, then 22-26 AWG, twisted pair, shielded cable shall be utilized, to a maximum distance of 3000 feet.

Part 5.	Warranty

5.1	Terms

A.	The manufacturer of the above specified equipment shall guarantee equipment of its manufacture, and bearing its identification to be free from defects in workmanship and material for a period of 24 months for electronics and 12 months for mechanical parts from date of delivery from the factory or authorized distributor under normal use and service and otherwise when such equipment is used in accordance with instructions furnished by the manufacturer and for the purposes disclosed in writing at the time of purchase, if any.

B.	In the event a component fails to perform as specified and having been returned to the manufacturer transportation charges prepaid, and is proven defective in service during the warranty period, the manufacturer shall repair or replace the defective part. Replaceable elastomeric parts and glass components are expendable and are not covered by any warranty.

Part 6.	Options

6.1	Related Equipment

A.	190851 Junction box for sensor cable extension.

B.	102535 Sensor extension cable, 24 AWG, 3 twisted pair, shielded.

C.	191006 Flow switch manifold for in-line applications.

D.	Calibration buffers (pH 4, 7 and 10).

Part 7.	Spare Parts

7.1	Recommended Spare Parts

- 103163 Fuse, 1 A, 250 VAC

- 102864 Fuse, 6 A, 250 VAC

- WEL-PHF-NN pH electrode cartridge

| #### Measurement Performance |  | Mechanical |  |
| --- | --- | --- | --- |
| Range | -2 to 16 pH ± 1500 mV (ORP) | Enclosure NEMA Rating | Polycarbonate NEMA 4X |
| Resolution | 0.0015 pH units (0.01 pH displayed) 92 V (1 mV displayed) (ORP) | Dimensions | 8.5" x 6.5" x 5.5" |
| Accuracy (Calibrated) | ± 0.01 pH ± 1 mV (ORP) | Display | 2 x 16 character backlit liquid crystal |
| Temp. Comp. (optional) | 100 or 1000 ohm platinum RTD | Ambient Temp. | 32 to 122F (0 to 50C) |
| Temperature Range | 32 to 212F (0 to 100C) | Storage Temp | -20 to 180F (-29 to 180C) |
| Temperature Resolution | ± 0.09F (0.05C) | Shipping Weight | 7 lbs (approximately) |
| Temperature Accuracy | ± 0.9F (0.5C) |  |  |

| ##### Inputs |  | ###### Outputs |  |
| --- | --- | --- | --- |
| Power Controller | 100-240 VAC, 50/60 Hz, 8A Fuse: 1.0 ampere, 5 x 20 mm | Control (On/Off) Internally powered relays | 6 A (resistive), 1/8 HP All relays are fused together as one group, total current for this group must not exceed 6A |
| pH preamp (supplied by controller) | ± 5 VDC, 5 mA | Control (Proportional) Solid state relays | 150 mA, 40 VDC maximum VLOWMAX = 0.13V @ 18 mA |
| Signal pH/ORP | ± 1500 mV | AUX1, AUX2, Alarm Dry contact relays | 6 A (resistive), 1/8 HP Dry contact relays are not fuse protected |
| Temp. Comp(optional) | Pt100 or Pt 1000 | 4-20mA (optional) | Fully isolated, internally powered, 600maximum resistive load. Resolution, .001% of span, Accuracy, ± 1% of reading |
| Interlock (optional) | Isolated dry contact closure required (i.e., flow, level, etc.) |  |  |

Dimensions

### Safety Approvals

The WPH series controllers are in compliance with the following safety and performance standards:

| Agency Approvals |  |
| --- | --- |
| UL | ANSI/UL 61010-1:2004, 2nd Edition* |
| CAN/CSA | C22,2 No.61010-1:2004 2nd Edition* |
| CE Safety | EN 61010-1:2001 2nd Edition * |
| CE EMC | EN 61326-1:2006 |
| Note: For EN61000-4-6, EN61000-4-3 the controller met performance criteria B. |  |
| *Class A equipment: Equipment suitable for use in establishments other than domestic, and those directly connected to a low voltage (100-240 VAC) power supply network which supplies buildings used for domestic purposes. |  |

WPH410 SERIES INSTALLATION – IN-LINE MOUNTING

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | AC POWER, 6 AMPS MAXIMUM, METERING PUMP, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| C | pH/ORP ELECTRODE, 4 x 24 AWG PLUS SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG PLUS SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL FLOW SWITCH, 2 x 24 AWG PLUS SHIELD, 5 FT SUPPLIED |
| E | OPTIONAL 4-20mA OUTPUT, 2 x 24 AWG PLUS SHIELD |
| F | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

WPH420 SERIES INSTALLATION – IN-LINE MOUNTING

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200 mA MAXIMUM, METERING PUMP, 2 x 22 AWG PLUS SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG PLUS SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG PLUS SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL FLOW SWITCH, 2 x 24 AWG PLUS SHIELD, 5 FT SUPPLIED |
| E | OPTIONAL 4-20mA OUTPUT, 2 x 24 AWG PLUS SHIELD |
| F | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

WPH410 SERIES INSTALLATION – SUBMERSION MOUNTING

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | AC POWER, 6 AMPS MAXIMUM, METERING PUMP, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| C | pH/ORP ELECTRODE, 4 x 24 AWG PLUS SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG PLUS SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL 4-20mA OUTPUT, 2 x 24 AWG PLUS SHIELD |
| E | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

WPH420 SERIES INSTALLATION – SUBMERSION MOUNTING

| A | AC POWER, 8 AMPS MAXIMUM, 2 x 18 AWG PLUS GROUND OR LOCAL CODE |
| --- | --- |
| B | PULSE OUTPUT, 400VDC 200mA MAXIMUM, METERING PUMP, 2 x 22 AWG PLUS SHIELD |
| C | pH/ORP ELECTRODE, 4 x 24 AWG PLUS SHIELD (OR IF A.T.C. OPTION 6 x 24 AWG PLUS SHIELD) 20 FT SUPPLIED |
| D | OPTIONAL 4-20mA OUTPUT, 2 x 24 AWG PLUS SHIELD |
| E | DRY RELAY CONTACT, 6 AMPS MAXIMUM (UNFUSED), ALARM DEVICE, WIRING DEVICE DEPENDENT, FOLLOW LOCAL CODE |

## WPH Series Ordering Information

WPH410/420  Controller

# WPH410 -

VOLTAGE

ELECTRODE

OUTPUT

| PART # / CODE | DESCRIPTION |
| --- | --- |
| WPH410 | pH/ORP Controller, on/off control outputs |
| WPH420 | pH/ORP Controller, proportional control outputs |
| voltage |  |
| 1 | 115 VAC, pre-wired with 6” pigtails (WPH410) or with 10’ cables (WPH420) |
| 3 | 115 VAC, pre-wired WPH420 with 10’ cables, with (2) E90495 connectors for EW pumps |
| 5 | Hardwired, cable glands |
| Note: To connect 10 ft. cables from WPH420 to EW-F pumps, order one E90495 connector per pump. |  |
| data output |  |
| N | No 4-20 mA output |
| 4 | Single Isolated 4-20 mA output |
| 2 | Two (2) Isolated 4-20 mA outputs |
| options |  |
| N | None |
| 1 | Preamplifier (190783) w/10’ cable, pre-wired |
| 2 | Submersion flat pH electrode w/preamp (WEL-PHF-21) |
| 3 | In-line flat pH electrode w/preamp (WEL-PHF-22) - includes 3/4” NPTF tee |
| 4 | In-line flat pH electrode, preamp (WEL-PHF-22) and flow switch mounted to panel |
| 4T | In-line flat pH electrode with ATC, preamp (WEL-PHF-12) and flow switch mounted to panel |
| 5 | Submersion ORP electrode w/preamp (WEL-MVF-21) |
| 6 | In-line ORP electrode w/preamp (WEL-MVF-22) - includes 3/4” NPTF tee |
| 6R | In-line rod style ORP electrode w/preamp (WEL-MVR-22) - includes 3/4” NPTF tee |
| 7 | In-line ORP electrode w/preamp (WEL-MVF-22) and flow switch mounted to panel |
| 7R | In-line rod style ORP electrode w/preamp (WEL-MVR-22) and flow switch mounted to panel |
| usb |  |
| N | Software upgrade capability only |
| U | Integrated datalogging and config file import/export via USB flash stick |
| NOTE: See the WEL Series pH/ORP Electrode prices for additional electrode options, such as bulb style pH, HF resistant pH, housings that provide automatic temperature compensation (ATC), and metric in-line mounting. To order: Order the WPH controller with the option “N”, then order the appropriate WEL electrode. Make sure to specify either WEL housing option 1 or 2, which contain a preamplifier. |  |

WPH410 Conduit Wiring

WPH420 Conduit Wiring

WPH Inputs using WEL pH/ORP Electrode Housings

WPH Inputs using pH/ORP Electrode/External Preamplifiers

WPH410 Outputs

WPH420 Outputs