# EJB09-31 Series Specifications

## 1.0	Scope

### 1.1	This specification in combination with pump data sheets identifies the minimum requirements for electronic metering pumps.

## 2.0	Reference codes and standards

### 2.1	Pumps shall comply with the latest editions of the following codes and standards:

#### UL Standard 778					
Hydraulic Institute Standards							
National Electric Code
NEMA 4X (IP65)

## 3.0	Definitions

3.1	Electronic metering pump-	A positive displacement diaphragm metering pump in which the diaphragm is actuated by an electromagnetic solenoid which is in turn controlled by an electronic circuit.

- General

  - Output volume shall be adjustable while pump is in operation.

  - Weight of pump as installed shall not exceed 4 pounds.

4.3	Pump shall fit within a rectangular volume 8.7” long by 4.0” wide by 8.2” high.

- Drive

5.1	The pump mechanism shall be totally enclosed with no exposed moving parts.

5.2	Electronic control module shall be located opposite the liquid end.

5.3	Average power consumption shall not exceed 15 watts under full speed and maximum pressure conditions.

5.4	Metering pump shall be capable of pumping a maximum of (Q) GPH against a maximum pressure of (P) PSI. (Q and P from Table 1).

5.5	Pump speed shall be adjustable from 1 to 360 strokes per minute by means of a readily accessible keypad with digital display and indication LED.

5.6	Control of pump speed shall be selectable between manual and external by means of push buttons.

5.7	Pump shall be able to be stopped and started by means of push buttons.

5.8	In manual mode, output is controlled by pump speed, adjustable from 1 to 360 strokes per minute set by keypad with digital display.

5.9	In external mode, pump speed is controlled 1:1 to external no-voltage digital input pulses.

5.10	Pump shall include an external stop input that can be set to stop the pump from a normally open no-voltage contact signal.  The display will visibly indicate “STOP” during a stopped condition.

5.11	Pump keypad shall be lockable to prevent tampering.

## 6.0	Materials of construction

### Pump housing shall be of chemically resistant glass fiber reinforced thermoplastic.

### All exposed fasteners shall be 316 stainless steel.

### 6.3	Liquid end materials shall be as shown in Table 2.

## 7.0	Shop tests

### 7.1	All pumps shall pass manufacturer’s standard performance test.

##### Table 1

| Size | Output Capacity (Q) |  | Max Output per stroke (mL) (Fixed) | Max Pressure (P) |  | Connection Size Tubing O.D. |
| --- | --- | --- | --- | --- | --- | --- |
|  | Gal/hr | ML/min |  | PSI | MPa | in |
| B09 | 0.3 | 19 | 0.053 | 175 | 1.2 | 3/8 |
| B11 | 0.5 | 30 | 0.083 | 150 | 1.0 | 3/8 |
| B16 | 0.8 | 50 | 0.139 | 90 | 0.6 | 3/8 |
| B21 | 1.3 | 80 | 0.222 | 45 | 0.3 | 3/8 |
| B31 | 2.4 | 150 | 0.417 | 30 | 0.2 | ½ |
| B31-L | 3.2 | 200 | 0.833 | 22 | 0.15 | ½ |

##### Table 2

| Liquid End | Pump Head & Fittings | Diaphragm | Valve Balls | Valve Seat | Valve Seals | Gasket | Tubing |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FC | PVDF | PTFE bonded to EPDM | CE | PCTFE | PTFE | PTFE | LLDPE |
| TC | PVDF |  | CE | FKM | FKM |  |  |
| TA | PVDF |  | CE | PCTFE | AFLAS® |  |  |
| PC | GFRPP |  | CE | FKM | FKM |  |  |
| PE | GFRPP |  | CE | EPDM | EPDM |  |  |
| PA | GFRPP |  | CE | PCTFE | AFLAS® |  |  |
| VC(A) | PVC |  | CE | FKM | FKM |  |  |
| VE(A) | PVC |  | CE | EPDM | EPDM |  |  |
| VF | PVC |  | PTFE | EPDM | EPDM |  |  |
| SHN | 316SS |  | 316SS | 316SS | ---- |  | N/A |

CE	Alumina ceramic	EPDM	Ethylene propylene diene monomer

FKM	Fluoroelastomer	GFRPP	Glass fiber reinforced polypropylene

PCTFE	Polychlorotrifluoroethylene	LLDPE	Linear-Low Density Polyethylene

PTFE	Polytetrafluoroethylene	PVC	Polyvinylchloride (translucent)

PVDF	Polyvinylidenefluoride	AFLAS®	Tetrafluoroethylene propylene copolymer

316SS	316 Stainless Steel

## 8.0 Dimensions

EJB09-21

EJB31

NOTES:

- Addition of a Multifunction Valve increases overall length by 0.10”

- Addition of a Multifunction Valve increases discharge height by 2.62”.

Addition of the Auto Degassing Valve increases discharge height by 1.82”.

- Addition of a Multifunction Valve increases overall liquid end height by 1.25”. Addition of the Auto Degassing Valve increases overall liquid end height by 1.82”.