# EZB11-C36 Series Specifications

## 1.0	Scope

### 1.1	This specification in combination with pump data sheets identifies the minimum requirements for electronic metering pumps.

## 2.0	Reference codes and standards

### 2.1	Pumps shall comply with the latest editions of the following codes and standards:

#### UL Standard 778					
Hydraulic Institute Standards							
National Electric Code
NEMA 4X (IP65)

## 3.0	Definitions

3.1	Electronic metering pump-	A positive displacement diaphragm metering pump in which the diaphragm is actuated by an electromagnetic solenoid which is in turn controlled by an electronic circuit.

- General

4.1	Output volume shall be adjustable while pump is in operation.

4.2	Weight of pump as installed shall not exceed 6 pounds.

4.3	Pump shall fit within a rectangular volume 8.4” long by 4.6” wide by 8.4” high.

- Drive

5.1	The pump mechanism shall be totally enclosed with no exposed moving parts.

5.2	Electronic control module shall be easily removable for mounting in a remote location.

5.3	Average power consumption shall not exceed 22 watts under full speed and maximum pressure conditions.

5.4	Metering pump shall be capable of pumping a maximum of (q) GPH against a maximum pressure of (p) PSI. (q and p from Table 1).

5.5	Pump speed shall be adjustable from 1 to 360 strokes per minute by means of a readily accessible keypad with digital display.

## 6.0	Materials of construction

### Pump housing shall be of chemically resistant glass fiber reinforced thermoplastic.

### All exposed fasteners shall be 316 stainless steel.

### 6.3	Liquid end materials shall be as shown in Table 2.

## 7.0	Shop tests

### 7.1	All pumps shall pass manufacturer’s standard performance test.

##### Table 1

| Size | Output Capacity (q) |  | Max Output per stroke (mL) (Fixed) | Max Pressure (P) |  | Connection Size Tubing O.D. |
| --- | --- | --- | --- | --- | --- | --- |
|  | Gal/hr | ML/min |  | PSI | MPa | in |
| B11 | 0.6 | 38 | 0.11 | 150 | 1.0 | 3/8 |
| B16 | 1.0 | 65 | 0.18 | 105 | 0.7 | 3/8 |
| B21 | 1.5 | 95 | 0.26 | 60 | 0.4 | 3/8 |
| B31 | 3.2 | 200 | 0.56 | 30 | 0.2 | ½ |
| C16 | 1.3 | 80 | 0.22 | 150 | 1.0 | 3/8 |
| C21 | 2.0 | 130 | 0.36 | 105 | 0.7 | 3/8 |
| C31 | 4.3 | 270 | 0.75 | 50 | 0.35 | ½ |
| C36 | 6.3 | 400 | 1.17 | 30 | 0.2 | ½ |

##### Table 2

| Liquid End | Pump Head & Fittings | Diaphragm | Valve Balls | Valve Seat | Valve Seals | Gasket | Tubing |
| --- | --- | --- | --- | --- | --- | --- | --- |
| FC | PVDF | PTFE bonded to EPDM | CE | PCTFE | PTFE | PTFE | PE |
| PC | GFRPP |  | CE | FKM | FKM |  |  |
| PE | GFRPP |  | CE | EPDM | EPDM |  |  |
| VC(A) | PVC |  | CE | FKM | FKM |  |  |
| VE | PVC |  | CE | EPDM | EPDM |  |  |
| TC | PVDF |  | CE | FKM | FKM |  |  |
| VF | PVC |  | PTFE | EPDM | EPDM |  |  |

CE	Alumina ceramic		EPDM	Ethylene propylene diene monomer

FKM	Fluoroelastomer		GFRPP	Glass fiber reinforced polypropylene

PCTFE	Polychlorotrifluoroethylene	PE	Polyethylene

PTFE	Polytetrafluoroethylene		PVC	Polyvinylchloride (translucent)

PVDF	Polyvinylidenefluoride

DIMENSIONS

All dimensions in inches

| Model |  |  |  |  | A | B | C | D | E | F | G | H | J | L | P & Q TUBING | W |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| EZB | 11 16 21 | D1 D2 | -VC -PC -TC | -VE -PE -VF | 3.21 | 0.87 | 0.08 | 3.54 | 1.46 (3.03)1 [1.83]2 | 0.20 | 5.91 [6.11]2 | 7.24 [8.39]2 | 1.02 | 7.44 (9.53)1 [7.81]2 | 3/8” O.D. | 3.94 |
|  |  |  | -FC |  | 3.21 | 0.87 | 0.08 | 3.54 | 0.51 | 0.20 | 6.09 | 6.83 | 1.00 | 6.50 | 3/8” O.D. | 3.94 |
|  | 31 |  | -VC -PC -TC | -VE -PE -VF | 3.21 | 1.02 | 0.08 | 3.54 | 0.87 | 0.20 | 6.75 | 8.00 | 0.32 | 7.01 | 1/2” O.D. | 3.94 |
|  |  |  | -FC |  | 3.21 | 1.02 | 0.08 | 3.54 | 0.63 | 0.20 | 6.85 | 6.85 | 0.24 | 6.77 | 1/2” O.D | 3.94 |
| EZC | 16 21 | D1 D2 | -VC -PC -TC | -VE -PE -VF | 4.13 | 0.94 | --- | 3.94 | 1.46 (3.03)1 [1.83]2 | 0.31 | 6.30 [6.50]2 | 7.64 [8.79]2 | 1.42 | 8.15 (10.24)1 [8.52]2 | 3/8” O.D. | 4.57 |
|  |  |  | -FC |  | 4.13 | 0.94 | --- | 3.94 | 0.51 | 0.31 | 6.48 | 7.44 | 1.39 | 7.20 | 3/8” O.D. | 4.57 |
|  | 31 36 |  | -VC -PC -TC | -VE -PE -VF | 4.13 | 1.10 | --- | 3.94 | 0.87 | 0.31 | 7.11 | 8.37 | 0.71 | 7.72 | 1/2” O.D. | 4.57 |
|  |  |  | -FC |  | 4.13 | 1.10 | --- | 3.94 | 0.63 | 0.31 | 7.44 | 7.44 | 0.63 | 7.48 | 1/2” O.D. | 4.57 |

1 Dimension with automatic air vent valve option			2 With Multifunction valve

| Mounting Dimensions | R | S | T | X | V | Z |
| --- | --- | --- | --- | --- | --- | --- |
| EZB all variations | 3.46 | 0.28 | 0.63 | 0.24 | 0.39 | 1.26 |
| EZC all variations | 3.94 | 0.59 | 1.18 | 0.28 | 0.59 | 1.18 |

Walchem, An Iwaki America Incorporated Company

5 Boynton Road   Holliston, MA 01746  USA  TEL:  508-429-1110    FAX:  508-429-7433    www.walchem.com

P/N E00162.A  10/2008